## Slide 1: PN System Redundancy with S7-1500 R/H and ET 200
Technical Details (Part 2)

## Slide 2: SIMATIC S7-1500 Redundant Systems Further technical slide sets
This document is part of a three-part set of slides
Part 1: Redundant Systems SIMATIC S7-1500 R/H
Part 2: PROFINET System Redundancy with S7-1500 R/H and ET 200
Part 3: Network configuration with S7-1500 R/H
This document
New
New with TIA Portal V18 / Firmware V3.0
Legend:

## Slide 3: PROFINET System Redundancy Concept
PROFINET System Redundancy
A system of redundant PN controllers and singular or redundant PN devices.
Three levels:
  PN Controller
  PROFINET network
  PN-Device
The redundancy of one layer is independent of the other layers.
PN Controller
PN Controller
PN Device
PROFINET Network
2 connections
PN Controller
PN Controller

## Slide 4: PROFINET System Redundancy Redundancy operating modes with PROFINET
Redundant PN Controller 1
Redundant PN Controller 2
Redundant PN Controller 1
Redundant PN Controller 2
IM
I/O
PN S2 Device
PN Controller
IM
I/O
IM
I/O
IM
PN IO Network
PN IO Network
PN IO Network
Details on PN System Redundancy operating modes: See https://support.industry.siemens.com/cs/ww/de/view/109756450
PN S1 Device
PN R1 Device
PN IO Network
PN S1 devices can also be operated on redundant controllers S7-1500 R/H with the "Switched S1" function
Without System Redundancy (S1)
System Redundancy S2
Single Interface Modul
1 Connection to the controller
Single Interface Modul
2 Connections to red. controllers
System Redundancy R1
Redundant Interface Module
2x1 Connection to red. Controller
No redundancy
Controller Redundancy
Controller Redundancy
Network Redundancy
IM Redundancy
S1
S2
R1
Availability

## Slide 5: PROFINET System Redundancy Redundancy operating modes with PROFINET
Without System Redundancy (S1)
With System Redundancy S2
With System Redundancy R1
Fault tolerance:
CPU (bumpless)
PROFINET Failure
Fault tolerance:
CPU (with bump)
PROFINET Failure
Fault tolerance:
CPU (bumpless)
PROFINET Failure
Interface Module
Subnet
S1
S2
R1
The system tolerates the following failures (Fault Tolerance)

## Slide 6: PROFINET System Redundancy Support of PN System Redundancy with SIMATIC S7-1500
 |  | S7-1500 (Non-redundant) | S7-1500R | S7-1500H
 | Operation of PN devices without System Redundancy | Yes | Yes (Switched S1) | Yes (Switched S1)
 | Operation of PN devices with S2 System Redundancy | Yes (S1 mode only) | Yes | Yes
 | Operation of PN devices with R1 System Redundancy | No | No | Yes from firmware V3.0 and TIA Portal V18
S1
S2
R1

## Slide 7: Switching behavior without System Redundancy
Scenario: Controller failure

## Slide 8: Switching behavior without PROFINET System Redundancy Initial Situation
Primary Controller
Backup
Controller
S1-Device
RUN
RUN
Standard AR
Primary CPUs has a Connection (AR) to the S1-Device
Process Values
Process values are exchanged
S1
PROFINET

## Slide 9: Switching behavior without PROFINET System Redundancy Scenario: A controller fails – switching process begins
Primary
Controller
S1-Device
RUN
Remaining controller takes over automatically.
There is no connection to the S1 device
Process Values
Transfer of process values is interrupted. Outputs go to "0" or to substitute value
I/O Data
S1
PROFINET
Standard AR

## Slide 10: Switching behavior without PROFINET System Redundancy Scenario: A controller fails - connection establishment
Primary
Controller
S1-Device
RUN
Connection to the S1 device is re-established
Process Values
Transfer of process values is interrupted1). Outputs go to "0" or to substitute value
I/O Data
1) Duration depends on the start-up behavior of the S1 device. Minimum approx. 600ms
S1
PROFINET
Standard AR

## Slide 11: Switching behavior without PROFINET System Redundancy Scenario: One Controller Fails - Operation Complete
Primary
Controller
S1-Device
RUN
Process Values
I/O Data
Remaining controller has a connection to the S1 device
Process values are exchanged
S1
PROFINET

## Slide 12: Switching behavior with System Redundancy S2
Scenario: Controller failure

## Slide 13: Switching behavior with PROFINET System RedundancyS2 Initial Situation
Primary Controller
Backup
Controller
S2-Device
RUN
RUN
Primary AR
Backup AR
Both CPUs have a Connection (AR) to the S2-Device
Process Values
Process values are exchanged
S2
PROFINET

## Slide 14: Switching behavior with PROFINET System RedundancyS2 Scenario: A controller fails – switching process begins
Primary
Controller
S2-Device
RUN
Primary AR
Backup AR
Remaining controller takes over automatically.
The existing connection is activated
Process Values
Process values are used for a very short time1) frozen:
I/O values remain at the last value
I/O Data
1) S7-1500R 300ms / S7-1500H 50ms
S2
PROFINET

## Slide 15: Switching behavior with PROFINET System RedundancyS2 Scenario: One Controller Fails - Operation Complete
Primary
Controller
S2-Device
RUN
Primary AR
Backup AR
Process Values
I/O Data
Remaining controller has a connection to the S2 device
Process values are exchanged
S2
PROFINET

## Slide 16: Switching behavior with System Redundancy R1
Scenario: Controller failure

## Slide 17: Switching behavior with PROFINET System RedundancyR1 Initial Situation
Primary Controller
Backup
Controller
R1-Device
Primary AR
Backup AR
Primary Controller is connected to Interface Module 1 (IM1)
Backup Controller is connected to Interface Module 2 (IM2)
Process Values
Process values are exchanged
R1
RUN
RUN
PROFINET
PROFINET
IM1
IM2

## Slide 18: Switching behavior with PROFINET System RedundancyR1 Scenario: A controller fails – switching process begins
Primary
Controller
R1-Device
Primary AR
Backup AR
Process Values
R1
RUN
PROFINET
PROFINET
IM1
IM2
Remaining controller takes over automatically.
The existing connection is activated
Process values are used for a very short time1) frozen:
I/O values remain at the last value
1) Duration approx. 40ms

## Slide 19: Switching behavior with PROFINET System RedundancyR1 Scenario: One Controller Fails - Operation Complete
Primary
Controller
R1-Device
Primary AR
Backup AR
Process Values
R1
RUN
PROFINET
PROFINET
IM1
IM2
Remaining controller has a connection to interface module 2
Process values are exchanged

## Slide 20: Switching behavior with System Redundancy R1
Scenario: Failure of a PROFINET interface module

## Slide 21: Switching behavior with PROFINET System RedundancyR1 Initial Situation
Primary Controller
Backup
Controller
R1-Device
Primary AR
Backup AR
Primary Controller is connected to Interface Module 1 (IM1)
Backup Controller is connected to Interface Module 2 (IM2)
Process Values
Process values are exchanged
R1
RUN
RUN
PROFINET
PROFINET
IM1
IM2

## Slide 22: Switching behavior with PROFINET System RedundancyR1 Scenario: An interface module fails – switching process begins
Primary Controller
Backup
Controller
R1-Device
Primary AR
Backup AR
Backup Controller enables connection to Interface-Module 2 (IM2)
Process Values
R1
RUN
RUN
PROFINET
PROFINET
IM1
IM2
Process values are used for a very short time1) frozen:
I/O values remain at the last value
1) Duration approx. 40ms

## Slide 23: Switching behavior with PROFINET System RedundancyR1 Scenario: An interface module fails - operation complete
Primary Controller
Backup
Controller
R1-Device
Primary AR
Backup AR
I/O data is transferred via sync line via the backup controller to the Primary controller.
There is no controller switching.
Process Values
R1
RUN
RUN
PROFINET
PROFINET
IM1
IM2
Process values are exchanged

## Slide 24: Siemens products with System Redundancy function
SIMATIC S7-1500 Redundant Systems

## Slide 25: PROFINET System Redundancy Siemens I/O systems with PN S2 function (I)
Product |  | Article
ET 200SP IM155-6 PN HF (FW>=4.2) IM 155-6MF (Multi Fieldbus) |  | 6ES7155-6AU01-0CN0 6ES7155-6AU30-0CN0 6ES7155-6MU00-0CN0
ET 200MP IM155-5 PN HF (FW>=4.2) Also with active backplane bus for pulling/plugging in operation |  | 6ES7155-5AA00-0AC0 6ES7590-0BL00-0AA0 The active backplane bus allows the pulling and plugging of ET 200MP modules while the CPU is in operation.
ET 200eco PN M12-L (from FW 1.1) |  | 6ES7 14*-6**00-0BB0
PN/PN coupler |  | 6ES7158-3AD10-0XA0
S2
Overview in detail: https://support.industry.siemens.com/cs/ww/en/view/102325771

## Slide 26: PROFINET System Redundancy Siemens I/O systems with PN S2 function (II)
Product |  | Article
ET 200SP HA IM155-6 PN HA (with Single IM) (without F-Modules) |  | 6DL1155-6AU00-0PM0
ET 200iSP IM 152-1PN (with Single IM) (without F-Modules) For use in Ex zone 1 |  | 6ES7152-1BA00-0AB0
SIMATIC CFU Compact Field Unit Enables the connection of PROFIBUS PA field devices |  | 6ES7655-5PX11-1XX0
S2

## Slide 27: PROFINET System Redundancy Siemens drives with PN S2 function
Product |  | Article
SINAMICS S120, S150, G130, G150 with CU310-2PN (FW >=5.1 HF1) (as GSDML) |  | 6SL3040-1LA01-0AA0
SINAMICS S120, S150, G130, G150 with CU320-2PN (FW >= 5.1 HF1) (as GSDML) |  | 6SL3040-1MA01-0AA0
An application example exists for configuring the SINAMICS drives on S7-1500R/H: https://support.industry.siemens.com/cs/ch/en/view/109744811
S2

## Slide 28: PROFINET System Redundancy Switches with PN S2 function
Product |  | Article
SCALANCE XC-200 series |  | 6GK5 2 . . - . . . 00 - 2 . C2
SCALANCE XP-200 Serie |  | 6GK5 2 . . - 0 . A00 - . . S6
SCALANCE XF204-2BA |  | 6GK5 204-2AA00-2GF2
SCALANCE X400 from FW 6.3 |  | 6GK5408-. G.00-2AM2 6GK5416-. G.00-2AM2
SCALANCE X500 from FW 6.3 |  | 6GK552 . - . . . 00 - . AR2
S2

## Slide 29: PROFINET System Redundancy Siemens I/O systems with PN R1 function
Product |  | Article
ET 200SP IM155-6 PN R1(with redundant IM) |  | 6ES7155-6AU00-0HM0
ET 200SP HA IM155-6 PN HA (with redundant IM) (without F-Modules) |  | 6DL1155-6AU00-0PM0
ET 200iSP IM155-6 PN HA (with redundant IM) (without F-Modules) |  | 6ES7152-1BA00-0AB0
R1

## Slide 30: System Redundancy R1 with ET 200SP
SIMATIC S7-1500 Redundant Systems

## Slide 31: PROFINET System Redundancy ET 200SP with System Redundancy R1
An ET 200SP R1 system consists of:
2x IM 155-6 PN R1
1x BU-Type M0
2x same bus adapters from the ET 200SP spectrum
1x SIMATIC system rail
Any IO modules
1
1
1
2
3
3
3
4
4
5
5
2
Notes: Hot swapping (module replacement during runtime of the CPU) is possible also with multiple modules through the use of the active backplane bus for the ET 200MP. Up to 12 S7-1500 / ET 200MP modules can be inserted per station.

## Slide 32: ET 200SP with System Redundancy R1 Ordering data
Designation | Article
IM 155-6 PN R1 | 6ES7155-6AU00-0HM0
BU Type M0 | 6ES7193-6BR00-0HM0
SIMATIC system rail, Length 482,6mm | 6ES7193-6MR00-0AA0
SIMATIC system rail, Length 530mm | 6ES7193-6MR00-0BA0
SIMATIC system rail, Length 830mm | 6ES7193-6MR00-0CA0
SIMATIC system rail, Length 2000mm | 6ES7193-6MR00-0DA0
1
2

## Slide 33: ET 200SP with System Redundancy R1 System Rail
Required when using the IM 155-6 PN R1
Tight dimensional tolerances for operating conditions under high mechanical stress (significantly better than dimensional tolerance standard EN 60715)
long-term stable surface treatment for optimum interference dissipation
stable design for self-supporting construction
integrated Bosch profile grooves (6mm profile grooves, B-type)

## Slide 34: Configuration System Redundancy R1
SIMATIC S7-1500 Redundant Systems

## Slide 35: Configuration System Redundancy R1 Option 1: Separate subnets
1 subnet is used between controller and IO device.
Advantage:
Same (symmetric) IP addresses in both networks can be used
Disadvantage:
No double-sided connection of S1 or S2 devices possible (via Y-Switch)

## Slide 36: Configuration System Redundancy R1 Option 2: Shared subnet
Controller and IO devices are connected to a common subnet
Advantage:
Allows two-sided connection of S1 or S2 devices via Y-Switch
Disadvantage:
No symmetric IP addresses possible

## Slide 37: Configuration System Redundancy R1 Option 2: Shared subnet – configuration with S1 and S2 IO devices
S2-Device
Y-Switch
R1-Device
Y-Switch Details: See Slides Part 3 "Network configuration with S7-1500 R/H“

## Slide 38: Configuration System Redundancy Display of the redundancy mode in the TIA Portal
In the network view, S1, S2 and R1 devices are displayed as "Multi-Assigned"
The distinction S1/S2/R1 is displayed in the "Mode" column in the "EA Communication" table.
Here: ET 200MP: S2 Redundancy

## Slide 39: Disclaimer
© Siemens 2022
Subject to changes and errors. The information given in this document only contains general descriptions and/or performance features which may not always specifically reflect those described, or which may undergo modification in the course of further development of the products. The requested performance features are binding only when they are expressly agreed upon in the concluded contract.
All product designations may be trademarks or other rights of Siemens AG, its affiliated companies or other companies whose use by third parties for their own purposes could violate the rights of the respective owner.

## Slide 40: Contact
Publisher: Siemens 2022