## Slide 1: Redundant Systems Network Configuration
Technical Details (Part 3)

## Slide 2: SIMATIC S7-1500 Redundant Systems Further technical slide sets
This document is part of a three-part set of slides
Part 1: Redundant Systems SIMATIC S7-1500 R/H
Part 2: PROFINET System Redundancy with S7-1500R/H and ET 200
Part 3: Network configuration with S7-1500 R/H
This document

## Slide 3: Network configuration with S7-1500R/H Overview
S7-1500R
PROFINET Topology
Controller
IO-Devices
System Redundancy1)
S2
S1
MRP Ring
MRP Ring
Line
S2
S1
H-Sync
S7-1500H/HF
Redundant MRP Ring
Redundant line
H-Sync
S7-1500H/HF
R1
S2
S1
Via Y-Switch
Additional Topologies
MRP-Interconnection
MRP-Interconnection, combined topology
From FW V3.0
From FW V3.0
From FW V3.0
1) Details: See slide set Part 2 – PROFINET System Redundancy with S7-1500R/H and ET 200SP
MRP-Interconnection, combined topology

## Slide 4: Configuration Examples S7-1500R

## Slide 5: Configuration Examples S7-1500R Ring Topology with MRP
MRP Ring
Ring Topology
MRP ring is a prerequisite - the CPUs must be part of the ring
R-CPUs must be set as "MRP Automanager"
If the ring is interrupted, MRP reconfiguration is triggered
No devices allowed in the connection between the two CPUs
Recommendation: Max. 16 devices in the ring
Connecting S1 Devices via a Switch 1)
Devices with more than two ports (e.g. switches) must support H-Sync forwarding
Sync
S1 Devices connected via switch
H-Sync Forwarding must be supported
1) Reason: S1 devices do not route the H-Sync telegrams during an MRP reconfiguration phase. This would lead to a high CPU cycle time if the segment was interrupted. See chapter "H-Sync Forwarding" in the system manual S7-1500R/H

## Slide 6: Configuration Examples S7-1500R Ring Topology – Supplemented with MRP Interconnection
MRP Ring
Ring coupling via MRP interconnection
MRP interconnection switches allow the coupling of multiple MRP rings: Ring on S7-1500R + up to 10 additional MRP rings
Thanks to redundant switch architecture, the coupled network remains functional even if one switch fails.
Can be used with the following SCALANCE switches: XR500, XM400, XC200, XF204-2BA, XP200
The requirement of the " H-Sync Forwarding " function applies only to the devices that are found in the ring of R-CPUs. Reason: There are no H-Sync telegrams in the additional MRP rings.
Sync
MRP Ring
No requirement for "H-sync forwarding" in coupled rings

## Slide 7: Configuration Examples S7-1500H with S2 Redundancy

## Slide 8: Configuration example S7-1500H with S2 Redundancy Example with ring topology
MRP Ring
H-Sync
Ring topology with S2 Redundancy
H-CPUs must be set as "MRP Automanager"
If the ring is interrupted, MRP reconfiguration is triggered
H-Sync
Primary
Backup
MRP Ring
Behavior in case of ring interruption

## Slide 9: Configuration example S7-1500H with S2 Redundancy Coupling of multiple MRP rings
Ring coupling via MRP interconnection
MRP interconnection switches allow the coupling of multiple MRP rings: Ring on S7-1500H + up to 10 additional MRP rings
Thanks to redundant switch architecture, the coupled network remains functional even if one switch fails.
Up to 50 devices can be connected per ring  The total number of participants of an R/H CPU can also be achieved without spur lines.
Can be used with the following SCALANCE switches: XR500, XM400, XC200, XF204-2BA, XP200
MRP Ring 1
MRP Ring 2
MRP Ring 3
MRP-i Switches.
Primary
Backup
H-Sync

## Slide 10: Configuration example S7-1500H with S2 Redundancy Example for Combined Topology – For example: Backbone-Ring
H-Sync
Connection to backbone ring
As of firmware V3.0, the ring no longer has to be routed through the CPUs
This allows connection to existing infrastructure
In the ring there is no restriction to 100MBit/s transmission speed
From FW V3.0 / V18
Backbone-Ring
1..10 Git/s

## Slide 11: Configuration examples S7-1500H with S2 Redundancy Example with line topology
From FW V3.0 / V18
H-Sync
Line topology with S2 Redundancy
MRP protocol is not used
If a distance in the ring is interrupted, IO data transmission takes place via the H-Sync line
Requires firmware version from V3.0 and TIA Portal from V18
H-Sync
Primary
Backup
Behavior in case of ring interruption

## Slide 12: Configuration example S7-1500H without PN devices Special case for operation without PROFINET devices
Required setup with firmware < V3.0
From FW V3.0 / V18
H-Sync
Operation without PROFINET devices
If no PROFINET devices (S1, S2, R1) are connected, the X1 interfaces of the CPUs from V3.0 no longer need to be connected
Examples: Exclusive communication via Open User Communication or Modbus/TCP (e.g. communication concentrator")
H-Sync
Primary
Backup
X1
X1

## Slide 13: Configuration Examples S7-1500H with R1 Redundancy
From firmware V3.0 and TIA Portal V18

## Slide 14: Configuration examples S7-1500H with R1 Redundancy Example with ring topology
MRP Ring
MRP Ring
From FW V3.0 / V18
Ring topology with R1 Redundancy
A separate ring is set up for each H-CPU
H-CPUs must be set as "MRP Automanager"
If a track in the ring is interrupted, MRP reconfiguration takes place
Separate networks – same (mirror-image) IP addresses can be used

## Slide 15: Configuration examples S7-1500H with R1 Redundancy Ring topology for S7-1500H – extended with MRP Interconnection
MRP Ring
MRP Ring
MRP Ring
MRP Ring
Redundant ring coupling via MRP interconnection
Redundant R1 rings can also be connected via MRP interconnection
Thanks to redundant switch architecture, the coupled network remains functional even if one switch fails.
Up to 50 devices can be connected per ring  The total number of participants of an H CPU can also be achieved without spur lines.
Can be used with the following SCALANCE switches: XR500, XM400, XC200, XF204-2BA, XP200

## Slide 16: Configuration examples S7-1500H with R1 Redundancy Example for Combined Topology –For example: Backbone-Ring
From FW V3.0 / V18
Connection to separate ring
R1 rings do not have to be passed through the CPU
This enables connection to existing redundant network infrastructure
In the rings there is no restriction to 100MBit/s transmission speed
Ring 1
Ring 2
Backbone Rings
1..10 Git/s

## Slide 17: Configuration examples S7-1500H with R1 Redundancy Unsupported Topology - Single R1 Ring
This topology is not supported because the availability is unfavorable: The probability of a fault in the ring is also twice as high as with an S2 setup due to twice the number of IMs

## Slide 18: Configuration examples S7-1500H with R1 Redundancy Example with line topology
From FW V3.0 / V18
Line topology with R1 Redundancy
Line topology is also supported for R1 setup
Up to 256 devices can be connected in this topology
The feeding of the PN line from different sides increases the availability in case of double line interruption
X
X
Single-sided feeding If both lines are interrupted, devices behind them fail
Feeding from two sides If both lines are interrupted, all devices can be reached

## Slide 19: Configuration examples S7-1500H with R1 Redundancy Combination of R1 and S1/S2 devices
Primary PLC
Backup PLC
R1 devices
Network 1
Network 2
Network 1+2
Y-Switch SCALANCE XF204-2BA DNA 6GK5204-0BA00-2YF2
MRP Ring (optional)
R1
S2
S1
R1 configurations can be extended with S2 or S1 devices using a Y-switch.
The prerequisite for this is the configuration in the TIA Portal on 1 subnet
Result: Unique IP addresses in Network 1+2 are required

## Slide 20: Configuration examples S7-1500H with R1 Redundancy Combination of R1 and S1/S2 devices on ring structures
In order to connect the Y-switch to MRP rings, additional switches are required.
To increase availability, the Y-Switch can also be designed redundantly "Redundant DNA".
In this case, an MRP ring must be used on the S1/S2 side.
Switch
Primary PLC
Backup PLC
Y-Switch
Switch
Primary PLC
Backup PLC
Switch
Y-Switch
Y-Switch
Y-Switch am MRP Ring
Redundanter Y-Switch am MRP Ring
R1
R1
S2
S1

## Slide 21: Configuration examples S7-1500H with R1 Redundancy IO devices that are connected to only one CPU
Fault
Behavior in case of CPU 2 failure
CPU 1
CPU 2
CPU 1
CPU 2
Only connected to CPU 1
Connected to both CPUs via R1
Only connected to CPU 2
IO-Device 1
IO-Device 2
IO-Device 3
IO-Device 1
IO-Device 2
IO-Device 3
In some cases, it is sufficient if S1/S2 devices are connected to only one of the two CPUs. Examples of this are switches that transmit diagnostic data to the controller via PROFINET.
A failure of the connected CPU also leads to the failure of the IO device!

## Slide 22: Configuration examples S7-1500H with R1 Redundancy IO devices that are connected to only one CPU - Configuration
1) If the operating mode is not adjusted, the switch is detected as failed by the disconnected CPU and a corresponding bus error and alarm is generated.
Assignment must be set to both CPUs
Operating mode must be changed from "S2" to "S1" 1)
Assignment to only CPU 1 leads to an error during translation!
Even if devices are connected to only one CPU they must be mapped to both CPUs

## Slide 23: System IP Address at S2 ring and line structure

## Slide 24: Network configuration with S7-1500 H Use of System IP with MRP Ring
Primary
System IP
Primary
System IP
Initial Situation
Fault
Behavior in case of ring interruption
Reconfiguration of the MRP Ring
IO data continues to be transferred
Communication between HMI panel and primary CPU is done via the remaining route
 HMI communication is maintained

## Slide 25: Network configuration with S7-1500 H Use of System IP with line topology
Primary
System IP
Primary
System IP
Initial Situation
Sortie
Behavior in case of ring interruption
IO data continues to be transferred
No more connection between HMI panel and primary CPU 1)
 Communication to HMI panel fails
Recommendation: Use the device IP address of the CPUs for HMI communication
1) Only IO data is forwarded via the H-Sync line but no IP communication

## Slide 26: System IP Address at R1 ring and line structure

## Slide 27: Configuration examples S7-1500H with R1 Redundancy Combination of R1 and HMI devices
Primary PLC
Backup PLC
R1 devices
Network 1
Network 2
Y-Switch SCALANCE XF204-2BA DNA 6GK5204-0BA00-2YF2
MRP Ring (optional)
R1
R1 configurations can be extended with HMI devices using a Y-switch.
HMI

## Slide 28: Configuration examples S7-1500H with R1 Redundancy Combination of R1 and HMI devices
Primary PLC
Backup PLC
R1 devices
Network 1
Network 2
Y-Switch SCALANCE XF204-2BA DNA 6GK5204-0BA00-2YF2
MRP Ring (optional)
R1
HMI
If the connection to the Y-Switch fails, the connected HMI device also fails in line topology.
Solution:
Use device IP addresses of the CPUs or build a ring structure

## Slide 29: Connection of subordinate components

## Slide 30: Network configuration with S7-1500 R/H Connection of subordinate controllers
Option 1:
Connection as iDevice in switched S1 mode
Not bumpless
currently only possible via GSD
S2
Option 2: Via PN/PN Coupler  Bumpless switching
S1
Option 3: Open user communication between H-System and subordinate controller
 With short interrupt
Open User Communication
Terms:
Bumpless: When switching the H-system, the outputs remain at the last value. The switching time is very short.
Primary
Backup
H-Sync

## Slide 31: Network configuration with S7-1500 R/H Connection of PROFIBUS DP slaves
S2
S1
PROFIBUS
PROFIBUS
Note: IE/PB Link and IE/PB LINK HA are currently not supported
Open User Communication
PROFIBUS
Option 1:
Connection as iDevice in switched S1 mode
Not bumpless
currently only possible via GSD
Primary
Backup
H-Sync
Option 2: Via PN/PN Coupler  Bumpless switching
Option 3: Open user communication between H-System and subordinate controller 1)
 With short interrupt

## Slide 32: R1 network configuration with S7-1500 H Connection of subordinate controllers
Primary PLC
Backup PLC
Network 1
Network 2
R1
Y-Switch
S2
S1
Option 1: Connection as iDevice in switched S1 mode
Not bumpless / only via GSD
Option 2: About PN/PN Coupler  Bumpless switching
Option 3: Open user communication between H-System and subordinate controller 1)
 With short interrupt

## Slide 33: R1 network configuration with S7-1500 H Connection of PROFIBUS DP slaves
Primary PLC
Backup PLC
Network 1
Network 2
R1
Y-Switch
S2
S1
Option 1: Connection as iDevice in switched S1 mode
Not bumpless / only via GSD
Option 2: Via PN/PN Coupler  Bumpless switching
Option 3: Open user communication between H-System and subordinate controller 1)
 With short interrupt
PROFIBUS
PROFIBUS
PROFIBUS

## Slide 34: Disclaimer
© Siemens 2022
Changes and errors excepted. The information in this document contains only general descriptions or performance characteristics, which do not always apply in the form described in the specific application or which may change due to further development of the products. The desired performance characteristics are only binding if they are expressly agreed upon conclusion of the contract.
All product names may be trademarks or other rights of Siemens AG, its affiliates or third parties, the use of which by third parties for their own purposes may infringe the rights of their respective owners.

## Slide 35: Contact
Publisher: Siemens 2022